## Master
| Building Support |  | Process Common |  | Booster and Lift Stations |  | Reservoirs and Wetwells |  | Valve Vaults |  | Wells |  | Waste Water Plants |  | Waste Water Plants |  | Water Plants |  | Water Plants
100 | Intrusion | 200 | Supply Pressure/Upstream | 300 | Jockey Pump | 400 |  | 500 | Excessive Flow | 600 |  | 700 |  | 800 |  | 900 |  | 1000
101 | Flood | 201 | Discharge Pressure/Downstream | 301 | Pump #1 | 401 | Reservoir/Wet Well Level #1 | 501 | Rate Control #1 | 601 | Well Pump #1 | 701 |  | 801 |  | 901 |  | 1001
102 | Smoke | 202 | Turn-out/By-pass Pressure | 302 | Pump #2 | 402 | Reservoir/Wet Well Level #2 | 502 | Rate Control #2 | 602 | Well Pump #2 | 702 |  | 802 |  | 902 |  | 1002
103 | Fire Sprinkler | 203 |  | 303 | Pump #3 | 403 |  | 503 | Rate Control #3 | 603 | Well Pump #3 | 703 |  | 803 |  | 903 |  | 1003
104 | Lower Explosive Limit (Wetwell) | 204 |  | 304 | Pump #4 | 404 |  | 504 | Rate Control #4 | 604 |  | 704 |  | 804 |  | 904 |  | 1004
105 | Sump Pump Lead Float | 205 | System/Discharge Flow | 305 | Pump #5 | 405 | Reservoir Flow | 505 | Rate Control #5 | 605 |  | 705 |  | 805 |  | 905 |  | 1005
106 | Sump Pump Lag Float | 206 | System/Discharge Flow | 306 | Pump #6 | 406 | Reservoir Flow | 506 | Rate Control #6 | 606 |  | 706 |  | 806 |  | 906 |  | 1006
107 | Sump Pump #1 | 207 | Turn-out Flow | 307 | Pump #7 | 407 |  | 507 | Rate Control #7 | 607 |  | 707 |  | 807 |  | 907 |  | 1007
108 | Sump Pump #2 | 208 |  | 308 | Pump #8 | 408 |  | 508 | Rate Control #8 | 608 |  | 708 |  | 808 |  | 908 |  | 1008
109 | UPS | 209 |  | 309 | Pump #9 | 409 |  | 509 | Rate Control #9 | 609 |  | 709 |  | 809 |  | 909 |  | 1009
110 | Facility Power | 210 |  | 310 | High Volume Pump | 410 | Reservoir Isolation Valve | 510 | Rate Control #10 | 610 |  | 710 |  | 810 |  | 910 |  | 1010
111 | Control Power | 211 | Distribution Pressure (Zone ---) | 311 | High Volume Pump Day Tank | 411 | Reservoir Fill Valve #1 | 511 | High Pressure Relief Valve #1 | 611 | Well Pump #1 Drawdown | 711 |  | 811 |  | 911 |  | 1011
112 | Battery | 212 | Distribution Pressure (Zone ---) | 312 | High Volume Pump Cooling System | 412 | Reservoir Fill Valve #2 | 512 | High Pressure Relief Valve #2 | 612 | Well Pump #2 Drawdown | 712 |  | 812 |  | 912 |  | 1012
113 | Transfer Switch | 213 | Distribution Pressure (Zone ---) | 313 | High Volume Pump Battery System | 413 |  | 513 | High Pressure Relief Valve #3 | 613 | Well Pump #3 Drawdown | 713 |  | 813 |  | 913 |  | 1013
114 | DeviceNet Power Supply | 214 | Distribution Pressure (Zone ---) | 314 | High Volume Pump Discharge Valve | 414 |  | 514 |  | 614 |  | 714 |  | 814 |  | 914 |  | 1014
115 | Generator | 215 | Distribution Pressure (Zone ---) | 315 |  | 415 |  | 515 |  | 615 |  | 715 |  | 815 |  | 915 |  | 1015
116 | Generator Battery | 216 | Distribution Pressure (Zone ---) | 316 |  | 416 |  | 516 |  | 616 |  | 716 |  | 816 |  | 916 |  | 1016
117 | Fuel Tank | 217 | Distribution Pressure (Zone ---) | 317 |  | 417 |  | 517 |  | 617 |  | 717 |  | 817 |  | 917 |  | 1017
118 | Day Tank | 218 | Distribution Pressure (Zone ---) | 318 |  | 418 |  | 518 |  | 618 |  | 718 |  | 818 |  | 918 |  | 1018
119 | 3-Phase Power Failure | 219 | Distribution Pressure (Zone ---) | 319 |  | 419 |  | 519 |  | 619 |  | 719 |  | 819 |  | 919 |  | 1019
120 | Building Temperature | 220 | Distribution Pressure (Zone ---) | 320 |  | 420 | Reservoir Cycle Pump | 520 |  | 620 |  | 720 |  | 820 |  | 920 | Primary Coagulant Tank Level | 1020
121 | Gas Heat | 221 | Distribution Flow (Zone ---) | 321 | Discharge Valve Pump #1 | 421 | Wetwell Level 1 High Float | 521 | Isolation Valve #1 | 621 | Well Pump #1 Discharge Valve | 721 |  | 821 |  | 921 | Primary Coagulant - Pump 1 | 1021
122 | Electric Heat, Main Building | 222 | Distribution Flow (Zone ---) | 322 | Discharge Valve Pump #2 | 422 | Wetwell Level 2 High Float | 522 | Isolation Valve #2 | 622 | Well Pump #2 Discharge Valve | 722 |  | 822 |  | 922 | Primary Coagulant - Pump 2 | 1022
123 | Electric Heat, Main Building | 223 | Distribution Flow (Zone ---) | 323 | Discharge Valve Pump #3 | 423 |  | 523 | Isolation Valve #3 | 623 | Well Pump #3 Discharge Valve | 723 |  | 823 |  | 923 | Primary Coagulant - Pump 3 | 1023
124 | Electric Heat, Second Room | 224 | Distribution Flow (Zone ---) | 324 | Discharge Valve Pump #4 | 424 |  | 524 | Isolation Valve #4 | 624 |  | 724 |  | 824 |  | 924 |  | 1024
125 | Low Temperature Override | 225 | Distribution Flow (Zone ---) | 325 | Discharge Valve Pump #5 | 425 |  | 525 | Isolation Valve #5 | 625 |  | 725 |  | 825 |  | 925 |  | 1025
126 | Low Temperature Override | 226 | Distribution Flow (Zone ---) | 326 |  | 426 |  | 526 | Isolation Valve #6 | 626 | Well Pump #1 Discharge Pressure | 726 |  | 826 |  | 926 |  | 1026
127 | Low Temperature Override | 227 | Distribution Flow (Zone ---) | 327 |  | 427 |  | 527 | Isolation Valve #7 | 627 | Well Pump #2 Discharge Pressure | 727 |  | 827 |  | 927 |  | 1027
128 | Ventilation | 228 | Distribution Flow (Zone ---) | 328 |  | 428 |  | 528 | Isolation Valve #8 | 628 |  | 728 |  | 828 |  | 928 |  | 1028
129 |  | 229 | Distribution Flow (Zone ---) | 329 |  | 429 |  | 529 | Isolation Valve #9 | 629 |  | 729 |  | 829 |  | 929 |  | 1029
130 | Intrusion, Outbuilding | 230 | Distribution Flow (Zone ---) | 330 |  | 430 |  | 530 |  | 630 |  | 730 | Sludge Density Meter | 830 |  | 930 |  | 1030
131 | Flood, Outbuilding | 231 | Water Temperature #1 | 331 | Pump #1 Discharge Pressure | 431 | Cathodic Protection Tank No. | 531 |  | 631 | Well Pump #1 Unloading Valve | 731 | Sludge Density Meter | 831 |  | 931 |  | 1031
132 | Smoke, Outbuilding | 232 | Water Temperature #2 | 332 | Pump #2 Discharge Pressure | 432 | Cathodic Protection Tank No. | 532 |  | 632 | Well Pump #2 Unloading Valve | 732 |  | 832 |  | 932 |  | 1032
133 | Fire Sprinkler, Outbuilding | 233 | Water Temperature #3 | 333 | Pump #3 Discharge Pressure | 433 |  | 533 |  | 633 | Well Pump #3 Unloading Valve | 733 |  | 833 |  | 933 |  | 1033
134 | Lower Explosive Limit (Drypit) | 234 | Water Temperature #4 | 334 | Pump #4 Discharge Pressure | 434 |  | 534 |  | 634 |  | 734 |  | 834 |  | 934 |  | 1034
135 | Sump Pump Lead Float | 235 |  | 335 | Pump #5 Discharge Pressure | 435 | Seismic Sensor | 535 |  | 635 |  | 735 |  | 835 |  | 935 |  | 1035
136 | Sump Pump Lag Float | 236 |  | 336 | Pump #6 Discharge Pressure | 436 |  | 536 |  | 636 | Well Pump #1 Pre-lube | 736 |  | 836 |  | 936 |  | 1036
137 | Sump Pump #1, Outbuilding | 237 |  | 337 | Pump #7 Discharge Pressure | 437 |  | 537 |  | 637 | Well Pump #2 Pre-lube | 737 |  | 837 |  | 937 |  | 1037
138 | Sump Pump #2, Outbuilding | 238 |  | 338 |  | 438 |  | 538 |  | 638 |  | 738 |  | 838 |  | 938 |  | 1038
139 |  | 239 |  | 339 |  | 439 |  | 539 |  | 639 |  | 739 |  | 839 |  | 939 |  | 1039
140 | Facility Power, Outbuilding | 240 |  | 340 | Vibration Monitoring | 440 |  | 540 | Mainline Valve | 640 |  | 740 |  | 840 |  | 940 |  | 1040
141 | Control Power, Outbuilding | 241 |  | 341 | Vibration Monitoring | 441 | Reservoir Tank Heater #1 | 541 | By-pass Valve | 641 | Well Pump #1 Flow | 741 |  | 841 |  | 941 |  | 1041
142 | Battery, Outbuilding | 242 |  | 342 | Vibration Monitoring | 442 | Reservoir Tank Heater #2 | 542 | Turn-out Valve | 642 | Well Pump #2 Flow | 742 |  | 842 |  | 942 |  | 1042
143 | Transfer Switch, Outbuilding | 243 |  | 343 | Vibration Monitoring | 443 | Reservoir Tank Heater #3 | 543 | Recharge Valve | 643 | Well Pump #3 Flow | 743 |  | 843 |  | 943 |  | 1043
144 | DeviceNet Power Supply | 244 |  | 344 | Vibration Monitoring | 444 |  | 544 |  | 644 |  | 744 |  | 844 |  | 944 |  | 1044
145 | Generator, Outbuilding | 245 |  | 345 | Vibration Monitoring | 445 |  | 545 | Recharge Flow | 645 |  | 745 |  | 845 |  | 945 |  | 1045
146 | Fuel Tank, Outbuilding | 246 |  | 346 |  | 446 |  | 546 |  | 646 |  | 746 |  | 846 |  | 946 |  | 1046
147 | Day Tank, Outbuilding | 247 |  | 347 |  | 447 |  | 547 |  | 647 |  | 747 |  | 847 |  | 947 |  | 1047
148 |  | 248 |  | 348 |  | 448 |  | 548 |  | 648 |  | 748 |  | 848 |  | 948 |  | 1048
149 |  | 249 |  | 349 |  | 449 |  | 549 |  | 649 |  | 749 |  | 849 |  | 949 |  | 1049
150 | Building Temperature, Outbuilding | 250 | Chlorine Analyzer | 350 |  | 450 |  | 550 | Emergency Valve | 650 |  | 750 |  | 850 |  | 950 |  | 1050
151 | Gas Heat, Outbuilding | 251 | Fluoride Analyzer | 351 | Pump #1 Discharge Flow | 451 | Reservoir Intrusion | 551 | Ring-Follower | 651 | Chemical Feed Pump #1, Chlorine | 751 | Chemical Feed Pump #1, Chlorine | 851 |  | 951 |  | 1051
152 | Electric Heat, Outbuilding | 252 | pH Analyzer | 352 | Pump #2 Discharge Flow | 452 | Reservoir Intrusion | 552 |  | 652 | Chemical Feed Pump #2, Chlorine | 752 | Chemical Feed Pump #2, Chlorine | 852 |  | 952 |  | 1052
153 | Electric Heat, Outbuilding | 253 | Dissolved Oxygen | 353 | Pump #3 Discharge Flow | 453 |  | 553 |  | 653 | Chlorine System | 753 | Chlorine System | 853 |  | 953 |  | 1053
154 |  | 254 | Turbidity Meter | 354 | Pump #4 Discharge Flow | 454 |  | 554 |  | 654 |  | 754 |  | 854 |  | 954 |  | 1054
155 | Low Temperature Override | 255 |  | 355 | Pump #5 Discharge Flow | 455 |  | 555 | Tunnel Pressure | 655 | Chemical Feed Pump #1, Fluoride | 755 | Sodium Bisulfite Feed System #1 | 855 |  | 955 |  | 1055
156 |  | 256 |  | 356 | Pump #6 Discharge Flow | 456 |  | 556 | Meter Cavity Pressure | 656 | Chemical Feed Pump #2, Fluoride | 756 | Sodium Bisulfite Feed System #2 | 856 |  | 956 |  | 1056
157 |  | 257 |  | 357 | Pump #7 Discharge Flow | 457 |  | 557 |  | 657 | Fluoride System | 757 | Sodium Bisulfite Tank Level #1 | 857 |  | 957 |  | 1057
158 | Ventilation, Outbuilding | 258 |  | 358 |  | 458 |  | 558 |  | 658 | Fluoride Saturator Tank Level | 758 | Sodium Bisulfite Tank Level #2 | 858 |  | 958 |  | 1058
159 |  | 259 |  | 359 |  | 459 |  | 559 |  | 659 |  | 759 |  | 859 |  | 959 |  | 1059
160 | Outside Ambient Temperature | 260 | Pneumatic Compressor (Air) | 360 |  | 460 |  | 560 |  | 660 | Sodium Hypochlorite Generator | 760 |  | 860 |  | 960 |  | 1060
161 |  | 261 |  | 361 | Pump Cooling Water | 461 |  | 561 | Hydraulic Pump #1 | 661 | Sodium Hypochlorite Tank Level | 761 |  | 861 |  | 961 |  | 1061
162 |  | 262 | Hydro-pneumatic Tank 1 | 362 |  | 462 |  | 562 | Hydraulic Pump #2 | 662 | Sodium Hypochlorite Transfer Pump #1 | 762 |  | 862 |  | 962 |  | 1062
163 |  | 263 | Hydro-pneumatic Tank 2 | 363 |  | 463 |  | 563 | Hydraulic System | 663 | Sodium Hypochlorite Transfer Pump #2 | 763 |  | 863 |  | 963 |  | 1063
164 | Generator Ventilation | 264 |  | 364 |  | 464 |  | 564 |  | 664 | Sodium Hypochlorite Dosing Pump #1 | 764 |  | 864 |  | 964 |  | 1064
165 |  | 265 | Water Heater Control | 365 |  | 465 |  | 565 |  | 665 | Sodium Hypochlorite Dosing Pump #2 | 765 |  | 865 |  | 965 |  | 1065
166 | Plant Air | 266 | Vibration Monitor | 366 |  | 466 |  | 566 |  | 666 |  | 766 |  | 866 |  | 966 |  | 1066
167 |  | 267 | Vibration Monitor | 367 |  | 467 |  | 567 |  | 667 |  | 767 |  | 867 |  | 967 |  | 1067
168 | Relay Panel Battery | 268 | Vibration Monitor | 368 |  | 468 |  | 568 | Hydrant | 668 | Brine Tank Level | 768 |  | 868 |  | 968 |  | 1068
169 | Relay Panel Power Supply | 269 | Vibration Monitor | 369 |  | 469 | Pump Supply Pressure Enable | 569 | Excessive Flow | 669 |  | 769 |  | 869 |  | 969 |  | 1069
170 |  | 270 |  | 370 |  | 470 |  | 570 |  | 670 |  | 770 |  | 870 |  | 970 |  | 1070
171 |  | 271 | Seal Water System #1 | 371 |  | 471 |  | 571 |  | 671 |  | 771 |  | 871 |  | 971 |  | 1071
172 |  | 272 | Seal Water System #2 | 372 |  | 472 |  | 572 |  | 672 |  | 772 |  | 872 |  | 972 |  | 1072
173 |  | 273 |  | 373 |  | 473 |  | 573 |  | 673 |  | 773 |  | 873 |  | 973 |  | 1073
174 |  | 274 |  | 374 |  | 474 |  | 574 |  | 674 |  | 774 |  | 874 |  | 974 |  | 1074
175 |  | 275 |  | 375 |  | 475 |  | 575 |  | 675 |  | 775 |  | 875 |  | 975 |  | 1075
176 |  | 276 |  | 376 |  | 476 |  | 576 |  | 676 |  | 776 |  | 876 |  | 976 |  | 1076
177 |  | 277 |  | 377 |  | 477 |  | 577 |  | 677 |  | 777 |  | 877 |  | 977 |  | 1077
178 |  | 278 |  | 378 |  | 478 |  | 578 |  | 678 |  | 778 |  | 878 |  | 978 |  | 1078
179 |  | 279 |  | 379 |  | 479 |  | 579 |  | 679 |  | 779 |  | 879 |  | 979 |  | 1079
180 |  | 280 |  | 380 |  | 480 |  | 580 |  | 680 |  | 780 |  | 880 |  | 980 |  | 1080
181 |  | 281 |  | 381 |  | 481 |  | 581 |  | 681 |  | 781 |  | 881 |  | 981 |  | 1081
182 |  | 282 |  | 382 |  | 482 |  | 582 |  | 682 |  | 782 |  | 882 |  | 982 |  | 1082
183 |  | 283 |  | 383 |  | 483 |  | 583 |  | 683 |  | 783 |  | 883 |  | 983 |  | 1083
184 |  | 284 |  | 384 |  | 484 |  | 584 |  | 684 |  | 784 |  | 884 |  | 984 |  | 1084
185 |  | 285 |  | 385 |  | 485 |  | 585 |  | 685 |  | 785 |  | 885 |  | 985 |  | 1085
186 |  | 286 |  | 386 |  | 486 |  | 586 |  | 686 |  | 786 |  | 886 |  | 986 |  | 1086
187 |  | 287 |  | 387 |  | 487 |  | 587 |  | 687 |  | 787 |  | 887 |  | 987 |  | 1087
188 |  | 288 |  | 388 |  | 488 |  | 588 |  | 688 |  | 788 |  | 888 |  | 988 |  | 1088
189 |  | 289 |  | 389 |  | 489 |  | 589 |  | 689 |  | 789 |  | 889 |  | 989 |  | 1089
190 |  | 290 |  | 390 |  | 490 |  | 590 |  | 690 |  | 790 |  | 890 |  | 990 |  | 1090
191 |  | 291 |  | 391 |  | 491 |  | 591 |  | 691 |  | 791 |  | 891 |  | 991 |  | 1091
192 |  | 292 |  | 392 |  | 492 |  | 592 |  | 692 |  | 792 |  | 892 |  | 992 |  | 1092
193 |  | 293 |  | 393 |  | 493 |  | 593 |  | 693 |  | 793 |  | 893 |  | 993 |  | 1093
194 |  | 294 |  | 394 |  | 494 |  | 594 |  | 694 |  | 794 |  | 894 |  | 994 |  | 1094
195 |  | 295 |  | 395 |  | 495 |  | 595 |  | 695 |  | 795 |  | 895 |  | 995 |  | 1095
196 |  | 296 |  | 396 |  | 496 |  | 596 |  | 696 |  | 796 |  | 896 |  | 996 |  | 1096
197 |  | 297 |  | 397 |  | 497 |  | 597 |  | 697 |  | 797 |  | 897 |  | 997 |  | 1097
198 |  | 298 |  | 398 |  | 498 |  | 598 |  | 698 |  | 798 |  | 898 |  | 998 |  | 1098
199 |  | 299 |  | 399 |  | 499 |  | 599 |  | 699 |  | 799 |  | 899 |  | 999 |  | 1099
Note on E2: Reese Cheney: Always the facility normal supply side.
Note on E4: Reese Cheney: Use this if there are three zones in the facility.
Note on E7: Reese Cheney: Always the facility normal supply side. We would usuall monitor the discharge.
Note on E9: Reese Cheney: Use this if there are three zones in the facility.
Note on E68: Reese Cheney: Please see 340-345 for vibration gear associated with pumps
Note on H33: Reese Cheney: For pressure transmitters located between the pump and its discharge valve.
Note on H34: Reese Cheney: For pressure transmitters located between the pump and its discharge valve.
Note on H35: Reese Cheney: For pressure transmitters located between the pump and its discharge valve.
Note on H36: Reese Cheney: For pressure transmitters located between the pump and its discharge valve.
Note on H37: Reese Cheney: For pressure transmitters located between the pump and its discharge valve.
Note on H38: Reese Cheney: For pressure transmitters located between the pump and its discharge valve.
Note on H39: Reese Cheney: For pressure transmitters located between the pump and its discharge valve.
Note on H42: Reese Cheney: Please see 265-269 for vibration not associated with a pump.
Note on H43: Reese Cheney: Please see 265-269 for vibration not associated with a pump.
Note on H53: Reese Cheney: For flow transmitters located between the pump and its discharge valve.
Note on H54: Reese Cheney: For flow transmitters located between the pump and its discharge valve.
Note on H55: Reese Cheney: For flow transmitters located between the pump and its discharge valve.
Note on H56: Reese Cheney: For flow transmitters located between the pump and its discharge valve.
Note on H57: Reese Cheney: For flow transmitters located between the pump and its discharge valve.
Note on H58: Reese Cheney: For flow transmitters located between the pump and its discharge valve.
Note on H59: Reese Cheney: For flow transmitters located between the pump and its discharge valve.
Note on Q28: Reese Cheney: This instrument is located between the pump and the discharge valve. Use 201 for system discharge pressure after the discharge valve.
Note on Q29: Reese Cheney: This instrument is located between the pump and the discharge valve. Use 201 for system discharge pressure after the discharge valve.