SECTION 22 14 29.16 – SUBMERSIBLE SUMP PUMPS

- GENERAL

  - THE REQUIREMENT

    - The CONTRACTOR shall provide submersible sump pumps and appurtenant work, complete and operable, in accordance with the Contract Documents.

    - The requirements of MASS Section 10.04 Article 4.20 and MASS Section 10.05 Articles 5.6, 5.7 & 5.8, apply to the WORK of this Section.

- *************************************************************************************************************

- NTS: The following paragraph pertains to Water Design

    - The Supplier shall examine the Site conditions, intended application, and operation of the pump system and recommend the pump which will satisfy the indicated requirements.

- End of Water Design

- *************************************************************************************************************

- *************************************************************************************************************

- NTS: The following paragraph pertains to Waste Water Design

    - The Supplier shall examine the Site conditions, intended application, and operation of the pump system, and ensure that the sump pump will fit in the existing sump.

- End of Waste Water Design

- *************************************************************************************************************

  - SUBMITTALS

    - The CONTRACTOR shall provide submittals in accordance with MASS Section 10.05 Article 5.6.

    - Provide complete Manufacturer’s information including dimensional drawings, parts list, material and operational specifications, wiring diagrams, installation requirements, and operation and maintenance information.

- PRODUCTS

- *************************************************************************************************************

- NTS: The following Article pertains to Water Design

  - SUMP PUMP

    - Provide the following sump pumps:

| Facility | Number Required | Phase | Voltage |
| --- | --- | --- | --- |

    - Operating Conditions:  The WORK of this Section shall be suitable for long term operation under the following conditions:

| - Duty | - Intermittent |
| --- | --- |
| - Drive | - Constant speed |
| - Ambient environment | - Indoors |
| - Ambient temperature, degrees F | - 40 to 80 |
| - Ambient relative humidity, percent | - 40 to 90 |
| - Fluid service | - Potable water with grit |
| - Fluid temperature, degrees F | - 38 to 60 |
| Maximum size of spheres to pass, in. dia | - 0.75 |

    - Performance Requirements:

| - Maximum shutoff head, ft | - 65 |
| --- | --- |
| - Design flow capacity, gpm | - 40 |
| - Design flow pump head, TDH ft | - 40 |
| - Maximum motor speed, rpm | - 3450 |
| - Minimum motor size, hp | - 3/4 |

    - Pump Dimensions:  2-inch NPT discharge size.

- End of Water Design

- *************************************************************************************************************

- *************************************************************************************************************

- NTS: The following Article pertains to Waste Water Design

- End of Waste Water Design

- *************************************************************************************************************

  - PUMP REQUIREMENTS

    - Construction:  Construction of submersible sump pumps shall conform to the following requirements:

| - Pump casing | - Cast iron |
| --- | --- |
| - Impeller | - Semi-open, non-clog cast iron |
| - Bearings | - Permanently lubricated ball and sleeve type |
| - Shaft | - Stainless steel |
| - Seal | - Mechanical seal |
| - Mounting Method | - As recommended by the Manufacturer |
| - Pump Connection | - Union |

    - Drive:  Enclosed, submerged, electric motor, 230-volt single-phase with capacitor start, or 208-volt three-phase, 60 Hz ac power supply, as required.

- *************************************************************************************************************

- NTS: The following paragraphs pertain to Water Design

    - Control:  Provide a sump pump controller in accordance with the Drawings and Specifications.

    - Electrical Connection:  Twist-lock plug and receptacle in accordance with Division 26.

- End of Water Design

- *************************************************************************************************************

- *************************************************************************************************************

- NTS: The following paragraphs pertain to Waste Water Design

    - Control:  Provide a sump pump float switch independent of the pump.

    - Electrical Connection:  Twist-lock plug and receptacle in accordance with Division 26 and the Drawings.

- End of Waste Water Design

- *************************************************************************************************************

- *************************************************************************************************************

- NTS: The following Article pertains to Water Design

  - AUTOMATIC FLOAT SWITCH ASSEMBLY

    - Float Switch:  Float switch shall be Allen-Bradley 840-A7, or equal.

    - Float Operator Assembly:  Provide stainless steel float operator assembly complete with rod (length as necessary for installation), float, adjustable start and stop collars, and mounting hardware.  Float operator assembly shall be Allen-Bradley 840-1AD, or equal.

- End of Water Design

- *************************************************************************************************************

  - PROTECTIVE COATING

    - Pumps shall have the Manufacturer’s standard corrosion-resistant coating for submerged service.

  - MANUFACTURERS, OR EQUAL

    - Goulds WE series Model 3885.

- *************************************************************************************************************

- NTS: The following paragraphs pertain to Waste Water Design

  - SPARE PARTS

    - Provide two (2) sump pump repair kits with seals, o-rings, and bearings.

- End of Waste Water Design

- *************************************************************************************************************

- EXECUTION

  - INSTALLATION

    - Pumping equipment shall be installed in existing sumps in accordance with the Shop Drawings and as indicated.

    - The pump discharge shall be re-connected to the existing discharge piping as necessary.  The CONTRACTOR shall provide all mechanical pipe fittings required for the connection.

    - Install a locking receptacle near the sump pump in accordance with Division 26.  Connect the twist-lock plug to the sump pump power cord and connect to the twist-lock receptacle.

- *************************************************************************************************************

- NTS: The following paragraph pertains to Water Design

    - Install the float switch assembly as shown on the Drawings.  Install sufficient rod guides to provide reliable switch operation.

- End of Water Design

- *************************************************************************************************************

END OF SECTION 22 14 29.16