SECTION 25 36 16 – MONITORING TRANSDUCERS

- GENERAL (NOT USED)

- PRODUCTS

  - GENERAL

    - Signal Output:  Outputs shall be current regulated 4-20 mA DC capable of driving 0 to 600 ohms.

    - All instruments shall be FM-approved, or equal.

  - ELECTRONIC POWER MONITOR

- *************************************************************************************************************

- NTS: The following paragraph pertains to Water Design

    - The electronic power monitor shall measure 3-phase power, power factor, current, voltage, voltage unbalance, frequency, demand, and Volt-Amp-reactive power.  The meter shall have a two-element connection, a two-and-one-half-element connection, and a three-element connection.  The meter shall provide an EtherNet output and a door-mounted display module.  Power supply shall be 24 VDC.  The meter shall be an Allen-Bradley Bulletin 1404-M505B-ENT Power Monitor 3000 with 1404-DM Display Module, or equal.

- End of Waste Water Design

- *************************************************************************************************************

- *************************************************************************************************************

- NTS: The following paragraph pertains to Waste Water Design

    - The electronic power monitor shall measure 3-phase power, power factor, current, voltage, voltage unbalance, frequency, demand, and Volt-Amp-reactive power.  The meter shall have a two-element connection, a two-and-one-half-element connection, and a three-element connection.  The meter shall provide an EtherNet output and a door-mounted display module.  Power supply shall be 24 VDC.  The monitor package shall include (3) split ring CTs for single-phase service and (4) split ring CTs for three-phase services.  The meter shall be an Allen-Bradley Bulletin 1404-M505B-ENT Power Monitor 3000 with 1404-DM Display Module, or equal.

- End of Waste Water Design

- *************************************************************************************************************

    - Provide the following power monitors:

| Tag No. | Location |
| --- | --- |

- *************************************************************************************************************

- NTS: The following Article pertains to Water Design

  - POWER (KW) TRANSDUCER

    - The power transducer shall combine a microprocessor based transducer with a high accuracy split-core instrument grade current transformer (CT) in a single unit.  Performance requirements are:

      - High accuracy +/-1 percent

      - 4-20 mA output

      - Loop supply power 24 VDC

      - Single or three phase

    - The transducers shall be from the H8040 series, three CT models, from Veris Industries, or equal.

    - Provide the following transducers:

| Tag No. | Location | Voltage | Max. Amps | Phase |
| --- | --- | --- | --- | --- |

- End of Water Design

- *************************************************************************************************************

  - DC SYSTEM VOLTAGE TRANSDUCER

    - The DC system voltage transducer shall provide a 4-20 mA output, fully isolated from input, proportional to a 0-50 VDC input.  Supply voltage shall be 24 VDC.  The transducer shall provide accuracy of 0.5% of span with a 250 ms response time.

    - Manufacturer:  CR Magnetics CR5320-50, or equal.

    - Install DC system voltage transducers as shown on the panel wiring diagrams.

  - PHASE FAILURE MONITOR

    - Single-phase monitors are to be Entrelec ESS mecotron model 2.430.831.12 voltage monitoring relay, or equivalent.  Supply voltage range shall be 220-240 VAC. Voltage measuring range shall be 50-500 VAC.  Provide the following single-phase monitor:

| Tag No. | Location |
| --- | --- |

- EXECUTION

  - GENERAL

    - All monitoring transducers shall be handled, installed, calibrated, loop-tested, precommissioned, and performance tested in accordance with the Manufacturer’s installation instructions and Section 40 90 00 – Process Control and Instrumentation Systems.

  - ELECTRONIC POWER MONITOR INSTALLATION

    - Installation of electronic power monitors shall include a shorting switch as recommended by the Manufacturer.

    - Power monitor display modules shall be door-mounted at eye level.

END OF SECTION 25 36 16