SECTION 26 22 00.05 – DRY TYPE TRANSFORMERS

- GENERAL

  - THE REQUIREMENT

    - The CONTRACTOR shall provide dry-type transformers, complete and operable, in accordance with the Contract Documents.

    - Single Manufacturer:  Like products shall be the end product of one manufacturer in order to achieve standardization of appearance, operation, maintenance, spare parts, and manufacturer’s services.

  - CONTRACTOR SUBMITTALS

    - General:  Submittals shall be in accordance with MASS Section 10.05 Article 5.6 and Section 26 05 00 – Electrical Work, General.

    - Shop Drawings

      - Transformers

        - Dimension drawings

        - Technical certification sheets

        - Drawing of conduit entry/exit locations

        - Transformer ratings, including:

          - Voltage

          - Continuous current

          - Basic impulse level for equipment over 600 volts

          - kVA

        - Descriptive bulletins

        - Product sheets

- PRODUCTS

  - GENERAL

    - Transformers

      - The transformers shall be dry-type, designed, manufactured, and tested in accordance with the latest applicable standards of ANSI and NEMA.

      - Transformers shall be UL-listed and bear the UL label.

  - TRANSFORMERS

    - Ratings

      - kVA and voltage ratings shall be as indicated.

      - Transformers shall be designed for continuous operation at rated kVA, for 24 hours a day, 365 days a year operation, with normal life expectancy as defined in ANSI C57.96 - Guide for Loading Dry Type Distribution and Power Transformers

      - Transformer sound levels shall not exceed the following ANSI and NEMA levels for self-cooled ratings:

- Up to 9 kVA	40 db

- 10 to 50 kVA	45 db

- 51 to 150 kVA	50 db

    - Construction

      - Insulation Systems

        - Transformers shall be insulated as follows:

          - 2 kVA and below:  150 degrees C insulation system based upon 80 degree C rise.

          - 3 to 15 kVA:  185 degrees C insulation system based upon 115 degrees C rise.  15 kVA and above:  220 degrees C insulation system based upon 150 degrees C rise.

        - Required performance shall be obtained without exceeding the above indicated temperature rise in a 40 degrees C maximum ambient.

        - All insulation materials shall be flame-retardant and shall not support combustion as defined in ASTM D 635 – Test Method for Rate of Burning and/or Extent and Time of Burning of Self-Supporting Plastics in a Horizontal Position.

      - Transformer windings shall be copper.

      - Transformers shall have four 2-1/2 percent taps, two above and two below 480 volts.

    - Drive Isolation transformers shall be sized per the table below:

| HP | KVA |
| --- | --- |
| 2 | 3 |
| 3 | 6 |
| 5 | 7.5 |
| 7.5 | 11 |
| 10 | 14 |
| 15 | 20 |
| 20 | 27 |
| 25 | 34 |
| 30 | 40 |
| 40 | 51 |
| 50 | 63 |
| 60 | 75 |
| 75 | 93 |
| 100 | 118 |
| 125 | 145 |
| 150 | 175 |
| 200 | 220 |
| 250 | 275 |
| 300 | 330 |
| 400 | 440 |
| 500 | 550 |

    - Manufacturers: Transformers shall be floor- or wall-mounted type by General Electric, Cutler-Hammer, Square D, or equal.

- EXECUTION

  - GENERAL

    - All WORK of this Section shall be installed as indicated in Section 26 05 00 – Electrical Work, General.

END OF SECTION 26 22 00.05