SECTION 26 36 05 – HEAVY-DUTY SAFETY SWITCHES

- GENERAL

  - THE REQUIREMENT

    - Furnish and install heavy-duty, double-throw safety switches for manual transfer of loads between alternate sources of supply and single-throw safety switches for motor disconnect.

  - CODES AND STANDARDS

    - The heavy-duty safety switches shall conform to the requirements of:

      - UL 98 – Enclosed Switches

  - SUBMITTALS

    - Provide outline drawings with dimensions, and equipment ratings for voltage, amperage and short circuit in accordance with MASS Section 10.05 Article 5.6.

- PRODUCTS

  - SAFETY SWITCH

    - The safety switches used as transfer switches shall be heavy-duty, manually operated, single-throw or double-throw switches, full load make or break rated.  Switches shall include a NO contact that is made in the A and B position.

    - Switch shall be UL listed for use as service equipment and is to be labeled for this application.

    - Switch shall have switch blades which are visible when the switch is OFF and the cover is open.

    - Lugs shall be front removable and UL listed for aluminum or copper.

    - All current carrying parts shall be plated to resist corrosion.

    - The UL listed short circuit current rating of the double throw switch shall be 10,000 rms symmetrical amperes.

    - Provisions for padlocking the switch in the OFF position shall be provided.

    - Motor disconnect switches installed in lift station pad mounted control panels shall be rotary disconnect switches Allen-Bradley Bulletin 194RF, or equal.

  - ENCLOSURE

    - The safety switch shall be furnished in a NEMA Type 1 enclosure with gray baked enamel paint which is electrodeposited on cleaned, phosphate pre-treated galvannealed steel.

    - The enclosure shall be supplied with a metal nameplate which includes ON-OFF-ON markings.

  - MANUFACTURERS

    - Safety switches shall be manufactured by Square D, Allen-Bradley, or equal.

- EXECUTION

  - INSTALLATION

    - The safety switch shall be installed in accordance with the Manufacturer’s requirements and recommendations.

END OF SECTION 26 36 05