SECTION 40 91 19.36 – TEMPERATURE MEASURING SYSTEMS

- GENERAL

  - THE REQUIREMENT

    - General:  The CONTRACTOR shall provide temperature measuring systems, complete and operable, in accordance with the Contract Documents.

    - The requirements of Section 40 90 00 – Process Control and Instrumentation Systems apply to this Section.

    - All instruments shall be FM approved.

- PRODUCTS

  - RESISTOR TEMPERATURE DETECTORS

    - Insertion type Resistor Temperature Detectors (RTDs) shall be 100 ohms nominal at 0 degree C, tip-sensitive, three-wire platinum in 0.25-inch Type 316 stainless steel sheath with watertight potting.  Time constant in agitated water shall not exceed 6.0 seconds.  RTD shall comply with International Practical Temperature Scale (IPTS)-68 standards.  Accuracy shall be plus or minus 0.1 degree C.  Temperature transmitters shall be 2-wire devices with continuously adjustable span and zero adjustments, solid state circuitry, and a 4-20 mA DC output linearly proportional to the indicated temperature span.  Where indicated with thermowells, RTDs shall be provided with 316 stainless steel thermowell, spring-loading device, extensions, union coupler, and explosion-proof aluminum connection head.  Union shall extend out beyond the pipe lagging.

    - Resistance temperature detector assemblies shall be:

      - For potable water: RdF Corporation model 2910-(0)-(100)-F-K transmitter complete with 21D-11-S-3-A-D-B-4 spring loaded probe, or equal.  Span shall be 0 degrees F to 200 degrees F.

    - Wall mounted sensors are to be solidly mounted using an appropriate bracket.

- *************************************************************************************************************

- NTS: The following paragraph pertains to Waste Water Design

    - Provide temperature sensors as shown on the Contract Drawings.

- End of Waste Water Design

- *************************************************************************************************************

- *************************************************************************************************************

- NTS: The following paragraph pertains to Water Design

      - For indoor ambient air: RdF Corporation model 2910-(-40)-(120)-F-K transmitter complete with 21D-11-S-3-A-D-B-4 spring loaded probe, or equal.

    - Insertion well mounted sensors are to be installed in existing RdF Corporation (model S2-3-1.5-0-C) thermowells that are suitable for potable water.  Note: If an alternative RTD temperature sensor is proposed that will not mount in the existing thermowell the CONTRACTOR must arrange for:

      - The OWNER to program a system shutdown so that the required insertion can be made to the pipework.

      - A certified CONTRACTOR, qualified to undertake work on potable water systems, to make the insertion.

      - The necessary disinfection equipment, materials and documented procedure, to ensure that no contamination of the water distribution system is made during the insertion process.

      - All at the CONTRACTOR’s expense.

    - The following RTD temperature measuring systems shall be provided:

| Tag No. | Location |  | Service |  | Range |  | Type |  | NEMA Rating |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

  - THERMOSTATS

    - The “tamper-proof” thermostat of steel construction is to be lockable to restrict operation to approximately 40 – 45 oF.  A long life, industrial grade single pole single throw mechanism is to be employed.  Differential sensitivity is to be approximately 3 oF.  The “tamper-proof” thermostat is to be a White-Rodgers 176-6, or equal.  The following “tamper-proof” low temperature override thermostats shall be provided:

| Tag No. | Location | Service | Range | Type |
| --- | --- | --- | --- | --- |

  - COOLING THERMOSTATS

    - Cooling thermostats are to be a long-life industrial grade single pole, double-throw type of steel construction.  Differential to be 3°F.  The cooling thermostat is to be a White-Rodgers 179-1, or equal.  The following cooling thermostats shall be provided:

| Tag No. | Location | Service | Range (°F) | Type |
| --- | --- | --- | --- | --- |

- End of Water Design

- *************************************************************************************************************

- EXECUTION

  - GENERAL

    - Temperature measuring systems shall be handled, installed, calibrated, loop-tested, precommissioned, and performance tested according to Section 40 90 00 – Process Control and Instrumentation Systems.

END OF SECTION 40 91 19.36