SECTION 40 91 23.13 – AIR FLOW MEASURING SYSTEMS

- GENERAL

  - THE REQUIREMENT

    - General:  The CONTRACTOR shall provide flow sensors, complete and operable in accordance with the Contract Documents.

    - The requirements of Section 40 90 00 – Process Control and Instrumentation Systems apply to this Section.

    - All instruments shall be UL-approved.

  - CONTRACTOR SUBMITTALS

    - Furnish submittals in accordance with MASS Section 10.05 Article 5.6 and Section 40 90 00 – Process Control and Instrumentation Systems.

- PRODUCTS

  - AIR FLOW SENSOR

    - The air flow sensor shall consist of a 24 VDC power, 4-20 ma, 4-wire air velocity transmitter suitable for clean air with a temperature range of -40 degrees F to 212 degrees F.  The sensor shall use a heated mass flow sensor with selectable ranges down to 250 FPS full scale and a resolution of 1 FPS.  The sensor shall be position insensitive capable of being mounted in vertical pipe 4 inches in diameter.  The unit shall be approximate size of a ¾” conduit body.  The sensor shall include a set of controls and indicators within the unit to set the measurement range, calibrate the device, and display the air velocity.  All wetted parts shall be stainless steel.

    - The unit shall be Dwyer Series 641, or equal.

    - Provide air flow sensors as shown on the Contract Drawings.

- EXECUTION

  - GENERAL

    - Flow sensors shall be handled, installed, calibrated, loop-tested, precommissioned, and performance tested according to Section 40 90 00 – Process Control and Instrumentation Systems.

  - INSTALLATION

    - Install the air flow sensor in accordance with the Manufacturer’s requirements.

END OF SECTION 40 91 23.13